## AMERISTAR® PERIMETER SECURITY USA INC.

## ATLAS Shallow Mount Bollards – M50 Bollard System

# Construction Specification 32 41 00

# PART 1 – GENERAL

1.01   WORK INCLUDED

The contractor shall provide all labor, materials and appurtenances necessary for installation of the anti-ram bollard system defined herein at (specify project site).

1.02   RELATED WORK

Section ___  ___  - Earthwork

Section ___  ___  - Concrete

1.03   SYSTEM DESCRIPTION

The manufacturer shall supply a total anti-ram bollard system of the Ameristar® Atlas M50 design.  The system shall include all components (i.e., levelers, bollard and base) required.

1.04   QUALITY ASSURANCE

The contractor shall provide laborers and supervisors who are thoroughly familiar with the type of construction involved and materials and techniques specified.

1.05   REFERENCES

- ASTM A106 – Standard Specification for Seamless Carbon Steel Pipe for High Temperature Service

- ASTM A572 – Standard Specification for High-Strength Low-Alloy Columbium-Vanadium Structural Steel

- ASTM A653/A653M - Standard Specification for Steel Sheet, Zinc-Coated (Galvanized) or Zinc-Iron Alloy Coated (Galvannealed) by the Hot-Dip Process.

- ASTM B117 - Practice for Operating Salt-Spray (Fog) Apparatus.

- ASTM D523 - Test Method for Specular Gloss.

- ASTM D714 - Test Method for Evaluating Degree of Blistering in Paint.

- ASTM D822 - Practice for Conducting Tests on Paint and Related Coatings and Materials using Filtered Open-Flame Carbon-Arc Light and Water Exposure Apparatus.

- ASTM D1654 - Test Method for Evaluation of Painted or Coated Specimens Subjected to Corrosive Environments.

- ASTM D2244 - Test Method for Calculation of Color Differences from Instrumentally Measured Color Coordinates.

- ASTM D2794 - Test Method for Resistance of Organic Coatings to the Effects of Rapid Deformation (Impact).

- ASTM D3359 - Test Method for Measuring Adhesion by Tape Test.

- ASTM F2656-15 – Standard Test Method for Vehicle Crash Testing of Perimeter Barriers

1.06   SUBMITTAL

The manufacturer’s literature shall be submitted prior to installation.

1.07   PRODUCT HANDLING AND STORAGE

Upon receipt at the job site, all materials shall be checked to ensure that no damage occurred during shipping or handling.  Materials shall be stored in such a manner to ensure proper ventilation and drainage, and to protect against damage, weather, vandalism, and theft.

PART 2 – MATERIALS

2.01   MANUFACTURER

A. The anti-ram single fixed bollard system shall conform to the Atlas M50/P_ design manufactured by Ameristar Perimeter Security Inc., in Tulsa, Oklahoma.  This system shall be M50/P_ based on crash-tested certified design.  Any engineering analysis needed for the Atlas system shall be based upon ASTM F2656-15, Impact Condition Designation M50, Penetration Rating P_, with the with capability of stopping a 15,000 lb. vehicle traveling at speeds up to 50 mph.

B. The anti-ram single bollard removable system shall conform to the Bulwark M50/P_ engineered design manufactured by Ameristar Perimeter Security Inc., in Tulsa, Oklahoma.  This system shall be M50/P_ Engineered based on test results of the Atlas M50 crash-tested certified Shallow Bollard system.  Engineering analysis shall be based upon ASTM F2656-15, Impact Condition Designation M50, Penetration Rating P_, with the with capability of stopping a 15,000 lb. vehicle traveling at speeds up to 50 mph.

C. The entire anti-ram bollard system, and all associated accessories and fittings shall be obtained from a single source.

2.02    MATERIAL

A.  Steel material for bollard base shall conform to the requirements of ASTM A992/A572 Grade 50 and ASTM A36.  Steel material for bollard tube shall comply with ASTM A500-13 Grade B&C.

B.  Bollard tube shall be a minimum 10.75” diameter with a multi-layer structural steel internally reinforcing rib.  Bollard assembly base shall be structural steel fabricated box of size and shape depicted on bollard system drawings.

2.03    FABRICATION

A.  Bollard system components shall be pre-cut to specified lengths and fabricated by welding.  Bollard assembly base box shall have pre-cut holes located per the design to allow for concrete flow and installation of reinforcement steel.  Assembly base shall have three self-leveling feet.

B.  Powder Coat option:  The manufactured bollard system shall be subjected to the PermaCoat® thermal stratification coating process (high-temperature, in-line, multi-stage, multi-layer) including, as a minimum, a six-stage pretreatment/wash, an electrostatic spray application of an epoxy base, and a separate electrostatic spray application of a polyester finish.  The base coat shall be a thermosetting epoxy powder coating (gray in color) with a minimum thickness of 2 mils (0.0508mm).  The topcoat shall be a “no-mar” TGIC polyester powder coat finish with a minimum thickness of 2 mils (0.0508mm).  The color shall be (specify black, bronze, white, or desert sand).

C.  Wet paint option:  The manufactured bollard system shall be subjected to a wet paint coating process including, a pretreatment/wash, a primer spray application base, and a separate topcoat application of a paint finish.

PART 3 - EXECUTION

3.01   PREPARATION

A.  The purchaser shall indicate the location of all bollards with suitable means.

B.  The purchaser shall indicate all underground utility locations, USC&G benchmarks, property monuments, and other underground structures.

C.  Before installing the Atlas bollards, all necessary site clearing and grading shall be performed by the purchaser.  An adequate clearance around entire bollard system layout is required.

3.02    INSTALLATION

A.  The bollard shall be installed per Ameristar System Drawings (supplied upon request).  Bollards shall be installed per product drawings and installation instructions.  The “Earthwork” and “Concrete” sections of this specification shall govern material requirements for the concrete footer unless otherwise specified by the product drawings or installation instructions.

B.  Rebar structure shall be installed as represented in the system drawings with a minimum 4000 psi concrete.  Shallow mount bollard system shall not exceed 13” bury depth.

3.03   CLEANING

The contractor shall clean the jobsite thoroughly to ensure it is left neat and free of any debris caused by the installation of the bollard system.